## Constants
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
20000 | shelf_no | 1 | WORD | 10 | x | total number of shelf
| snsr_no | 1 | WORD | 152
| snsr_data_reg_size | 1 | WORD | 6
| k_shelf_reg_size | 1 | WORD | 12 | x | how many register one shelf_data occupies
| k_shelf_modeIndexOffset | 1 | WORD | 0 |  | offset from shelf_x_addr to get shelf_x_mode
| k_shelf_autoWaterOnIndexOffset | 1 | WORD | 1 |  | offset from shelf_x_addr to get shelf_x_autoWaterOn
| k_shelf_autoLightOnIndexOffset | 1 | WORD | 2 |  | offset from shelf_x_addr to get shelf_x_autoLightOn
| k_shelf_autoLightIntensOffset | 1 | WORD | 3 |  | offset from shelf_x_addr to get shelf_x_autoLightIntens
| k_shelf_semiPVOnIndexOffset | 1 | WORD | 4 |  | offset from shelf_x_addr to get shelf_x_semiPVOn
| k_shelf_semiLightOnIndexOffset | 1 | WORD | 5 |  | offset from shelf_x_addr to get shelf_x_semiLightOn
| k_shelf_manuLightOnIndexOffset | 1 | WORD | 6 |  | offset from shelf_x_addr to get shelf_x_manuLightOn
| k_shelf_manuLightIntensIndexOffset | 1 | WORD | 7 |  | offset from shelf_x_addr to get shelf_x_manuLightIntens
| k_shelf_manuPvPosIndexOffset | 1 | WORD | 8 |  | offset from shelf_x_addr to get shelf_x_manuPVPos
| k_shelf_baseAddr | 1 | WORD | 10000 |  | baseAddr of all shelves
| PVLookup_1_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | PV look-up values when only 1 valves are on
| PVLookup_2_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | PV look-up values when only 2 valves are on
| PVLookup_3_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | PV look-up values when only 3 valves are on
| PVLookup_4_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | PV look-up values when only 4 valves are on
| ShelfSectionMapping_0_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | configure which shelves should belong to sec0
| ShelfSectionMapping_1_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | configure which shelves should belong to sec1
| ShelfSectionMapping_2_Arr | 4 | ARRAY [4] OF WORD | [4(0)] | x | configure which shelves should belong to sec2
| secModeArr | 3 | ARRAY [3] OF WORD | [3(0)] | x | secMode[0] : section 0 mode etc.
| sectionPvOnCountArr | 3 | ARRAY [3] OF WORD | [3(0)] |  | secPvCountArr[0]: number of PV to turn on in section 0
| k_sectionNo | 1 | WORD | 3 |  | total number of sections
| k_sectionMaxShelfNo | 1 | WORD | 4 |  | maximum number of shelves per section
| flowratePerShelf_local | 1 | WORD | 32 |  | flowrate per shelf in lpm
| k_enablePumpRedundancy | 1 | BOOL | FALSE |  | whether to enable pump redundancy
| main_current_state | 4 | ARRAY [4] OF INT | [4(0)] |  | Main state machine current state (for each instance)
| main_next_state | 4 | ARRAY [4] OF INT | [4(0)] |  | Main state machine next state (for each instance)
| transition_current_state | 4 | ARRAY [4] OF INT | [4(0)] |  | PV transition state machine current state (for each instance)
| transition_next_state | 4 | ARRAY [4] OF INT | [4(0)] |  | PV transition state machine next state (for each instance)
| PVChangeMode | 1 | INT | 0
| delay_counter | 4 | ARRAY [4] OF WORD | [4(0)] |  | Counter for delays
| bad_sector | 10 | ARRAY [10] OF WORD | [10(0)] |  | Bad sectors
| lastPVvalue | 10 | ARRAY [10] OF WORD | [10(0)] |  | Store last PV value for comparison whether to run PV change sequence or not
| pump_rampup_current_state | 3 | ARRAY [3] OF INT | [3(0)] |  | Pump ramp up state machine state
| pump_rampup_next_state | 3 | ARRAY [3] OF INT | [3(0)] |  | Pump ramp up state machine next state
| pump_rampup_current_value | 3 | ARRAY [3] OF WORD | [3(0)] |  | Pump ramp up value
| lastPumpTargetValue | 3 | ARRAY [3] OF WORD | [3(0)] |  | Pump ramp up previous value
| bRunPumpRampup | 3 | ARRAY [3] OF BOOL | [3(FALSE)] |  | Flag for each pump
| stat_water_vfd_power1 | 1 | BOOL | TRUE | x | Status for VFD power
| stat_water_vfd_comm1 | 1 | BOOL | TRUE | x | Status for VFD Comm
| stat_water_vfd_motor1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_vfd_pid1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_vfd_overload1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_vfd_other1 | 1 | BOOL | TRUE | x | Other VFD error
| stat_water_shelf_valvefault1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_shelf_overflow1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_temp_range1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_tank_levellow1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_tank_levelhigh1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_tank_sensor_unison1 | 1 | BOOL | TRUE | x | Status for water system
| stat_light_burned1 | 1 | BOOL | TRUE | x | Status for lighting system
| stat_light_powertrip1 | 1 | BOOL | TRUE | x | Status for lighting system
| stat_vent_vfd_comm1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_vfd_power1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_vfd_motor1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_vfd_overload1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_vfd_status_code | 1 | WORD | 0 | x | Ventilation VFD status code
| stat_vent_air_offline1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_air_deviation1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_air_humidity1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_air_co2 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_vent_air_temp1 | 1 | BOOL | TRUE | x | Status for ventilation system
| stat_alarm_clear | 1 | BOOL | TRUE | x | Global alarm indicator
| stat_plc1_system | 1 | BOOL | TRUE | x | PLC1 system
| stat_plc2_system | 1 | BOOL | TRUE | x | PLC2 system
| stat_plc1_io | 1 | BOOL | TRUE | x | PLC1 IO
| stat_plc2_io | 1 | BOOL | TRUE | x | PLC2 IO
| stat_plc_transfer | 1 | BOOL | TRUE | x | Transfer between PLC1 and PLC2
| tmpCounter | 1 | INT | 0
| ventilationCheckCounter | 1 | WORD | 0 |  | How frequent we read the sensors
| CONST_AIR_TEMPERATURE_MAX | 1 | WORD | 0 | x | For range checking
| CONST_AIR_TEMPERATURE_MIN | 1 | WORD | 0 | x | For range checking
| CONST_AIR_HUMIDITY_MAX | 1 | WORD | 0 | x | For range checking
| CONST_AIR_HUMIDITY_MIN | 1 | WORD | 0 | x | For range checking
| CONST_AIR_CO2_MAX | 1 | WORD | 0 | x | For range checking
| CONST_AIR_CO2_MIN | 1 | WORD | 0 | x | For range checking
| CONST_WATER_RANGE_MAX | 1 | WORD | 0 | x | Checking water temperature range
| CONST_WATER_RANGE_MIN | 1 | WORD | 0 | x | Checking water temperature range
| bRunAirflowController | 1 | BOOL | TRUE |  | Temporary flag to avoid running the code everytime
| airflowVfdSetPoint | 1 | WORD | 3000 | x | Airflow target setting
| airflowVfdOnOff | 1 | BOOL | TRUE | x | Airflow on/off
| tmpReal | 2 | REAL | 0
| pumpFillDrainMode | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Operation mode (FALSE - steady water supply, TRUE - on off mode)
| pumpFillDrainModeOn | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Turn on or off fill-drain mode
| pumpFillValue | 3 | ARRAY [3] OF WORD | [3(0)] | x | Fill-Drain mode Fill values
| pumpDrainValue | 3 | ARRAY [3] OF WORD | [3(0)] | x | Fill-Drain mode Drain values
| pumpFillModeFlag | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Whether it's currently in Fill mode (0) or Drain mode (1)
| pumpFillDrainTimer_s | 3 | ARRAY [3] OF WORD | [3(0)] |  | Temporary counter in seconds to determine the duration of fill and drain
| pumpFillDrainSecondCounter | 3 | ARRAY [3] OF WORD | [3(0)] |  | Temporary counter to get a duration in seconds
| pumpFillDuration_s | 3 | ARRAY [3] OF WORD | [3(0)] | x | Fill duration in seconds
| pumpDrainDuration_s | 3 | ARRAY [3] OF WORD | [3(0)] | x | Drain duration in seconds
| flowratePerShelf | 3 | ARRAY [3] OF WORD | [3(32)] | x | flowrate per shelf in lpm
| pumpFillDrainCountDownTimer_s | 3 | ARRAY [3] OF WORD | [3(0)] | x | Countdown timer
| pumpAbnormalFlag | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Flag idicate something is abnormal
| pumpAbnormalityStartTime | 3 | ARRAY [3] OF WORD | [3(0)] |  | Anormality start time

## Shelf
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
10000 | mode | 1 | WORD | 2 | x | shelf_x mode auto-1, semi-2, manual-3 | If there's any changes made here, please update accordingly in CONSTANTS sheet
| autoWaterOn | 1 | BOOL | FALSE | x
| autoLightOn | 1 | BOOL | FALSE | x
| autoLightIntensity | 1 | WORD | 0 | x
| semiPVOn | 1 | BOOL | FALSE | x
| semiLightOn | 1 | BOOL | FALSE | x
| manuLightOn | 1 | BOOL | FALSE | x
| manuLightIntensity | 1 | WORD | 0 | x
| manuPVPos | 1 | WORD | 0 | x
| exePVPos | 1 | WORD | 0
| exeLightIntensity | 1 | WORD | 0
| exeLightOn | 1 | WORD | 0

## Sensor List
base_addr | shelf_sensor | general_sensor
12000 | wPres0 | wFlow0
| wPres1 | wFlow1
| wPres2 | aFlow0
| wTemp0 | aFlow1
| wTemp1 | aFlow2
aFlow3
aFlow4
aFlow5
aFlow6
aFlow7
aFlow8
aFlow9
aFlow10
aFlow11
aFlow12
aFlow13
aFlow14
aFlow15
aFlow16
aFlow17
aFlow18
aFlow19
aFlow20
aFlow21
aFlow22
aFlow23
aFlow24
aTemp0
aTemp1
aTemp2
aTemp3
aTemp4
aTemp5
aTemp6
aTemp7
aTemp8
aTemp9
aTemp10
aTemp11
aTemp12
aTemp13
aTemp14
aTemp15
aTemp16
aTemp17
aTemp18
aTemp19
aTemp20
aTemp21
aTemp22
aTemp23
aTemp24
aCO2_0
aCO2_1
aCO2_2
aCO2_3
aCO2_4
aCO2_5
aCO2_6
aCO2_7
aCO2_8
aCO2_9
aCO2_10
aCO2_11
aCO2_12
aCO2_13
aCO2_14
aCO2_15
aCO2_16
aCO2_17
aCO2_18
aCO2_19
aCO2_20
aCO2_21
aCO2_22
aCO2_23
aCO2_24
aRH_0
aRH_1
aRH_2
aRH_3
aRH_4
aRH_5
aRH_6
aRH_7
aRH_8
aRH_9
aRH_10
aRH_11
aRH_12
aRH_13
aRH_14
aRH_15
aRH_16
aRH_17
aRH_18
aRH_19
aRH_20
aRH_21
aRH_22
aRH_23
aRH_24

## Sensor Data
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
- | value | 1 | WORD | 0
| state | 1 | WORD | 0
| err_u | 1 | WORD | 0
| warn_u | 1 | WORD | 0
| warn_l | 1 | WORD | 0
| err_l | 1 | WORD | 0

## Pump
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment
11000 | pump_e_OnArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_e_ValveOnArr | 1 | ARRAY [4] OF BOOL | [4(FALSE)] | x
| pump_e_FlowOrRpm | 1 | WORD | 0 | x | 1 - Flow, 2 - RPM
| pump_e_SetpointArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_h_Mode | 1 | WORD | 0 | x
| pump_h_PumpSelect | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_h_FlowSetArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_h_RpmSetArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_ctrlModeFbkArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_runningFbkArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_flowrateFbkArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_rpmFbkArr | 3 | ARRAY [3] OF WORD | [3(0)] | x

## IO Mapping
variable_name | addr | type | init_value | hmi_tag | comment
IO_waterPres_s0_0 | D28002 | WORD | -1
IO_waterPres_s0_1 | D28004 | WORD | -1
IO_waterPres_s0_2 | D28006 | WORD | -1
IO_waterPres_s1_0 | D28008 | WORD | -1
IO_waterPres_s1_1 | D28010 | WORD | -1
IO_waterPres_s1_2 | D28012 | WORD | -1
IO_waterPres_s2_0 | D28014 | WORD | -1
IO_waterPres_s2_1 | D28016 | WORD | -1
IO_waterPres_s2_2 | D28022 | WORD | -1
IO_waterPres_s3_0 | D28024 | WORD | -1
IO_waterPres_s3_1 | D28026 | WORD | -1
IO_waterPres_s3_2 | D28028 | WORD | -1
IO_waterPres_s4_0 | D28030 | WORD | -1
IO_waterPres_s4_1 | D28032 | WORD | -1
IO_waterPres_s4_2 | D28034 | WORD | -1
IO_waterPres_s5_0 | D28036 | WORD | -1
IO_waterPres_s5_1 | D28042 | WORD | -1
IO_waterPres_s5_2 | D28044 | WORD | -1
IO_waterPres_s6_0 | D28046 | WORD | -1
IO_waterPres_s6_1 | D28048 | WORD | -1
IO_waterPres_s6_2 | D28050 | WORD | -1
IO_waterPres_s7_0 | D28052 | WORD | -1
IO_waterPres_s7_1 | D28054 | WORD | -1
IO_waterPres_s7_2 | D28056 | WORD | -1
IO_waterPres_s8_0 | D28062 | WORD | -1
IO_waterPres_s8_1 | D28064 | WORD | -1
IO_waterPres_s8_2 | D28066 | WORD | -1
IO_waterPres_s9_0 | D28068 | WORD | -1
IO_waterPres_s9_1 | D28070 | WORD | -1
IO_waterPres_s9_2 | D28072 | WORD | -1
IO_flowmeter_0 | D28082 | WORD | -1
IO_flowmeter_1 | D28084 | WORD | -1
IO_propValve_s0_0 | D28102 | WORD | -1
IO_propValve_s0_1 | D28104 | WORD | -1
IO_propValve_s0_2 | D28106 | WORD | -1
IO_propValve_s1_0 | D28108 | WORD | -1
IO_propValve_s1_1 | D28122 | WORD | -1
IO_propValve_s1_2 | D28124 | WORD | -1
IO_propValve_s2_0 | D28126 | WORD | -1
IO_propValve_s2_1 | D28128 | WORD | -1
IO_propValve_s2_2 | D28142 | WORD | -1
IO_propValve_s3_0 | D28144 | WORD | -1
IO_propValve_s3_1 | D28146 | WORD | -1
IO_propValve_s3_2 | D28148 | WORD | -1
IO_propValve_s4_0 | D28162 | WORD | -1
IO_propValve_s4_1 | D28164 | WORD | -1
IO_propValve_s4_2 | D28166 | WORD | -1
IO_propValve_s5_0 | D28168 | WORD | -1
IO_propValve_s5_1 | D28182 | WORD | -1
IO_propValve_s5_2 | D28184 | WORD | -1
IO_propValve_s6_0 | D28186 | WORD | -1
IO_propValve_s6_1 | D28188 | WORD | -1
IO_propValve_s6_2 | D28202 | WORD | -1
IO_propValve_s7_0 | D28204 | WORD | -1
IO_propValve_s7_1 | D28206 | WORD | -1
IO_propValve_s7_2 | D28208 | WORD | -1
IO_propValve_s8_0 | D28222 | WORD | -1
IO_propValve_s8_1 | D28224 | WORD | -1
IO_propValve_s8_2 | D28226 | WORD | -1
IO_propValve_s9_0 | D28228 | WORD | -1
IO_propValve_s9_1 | D28242 | WORD | -1
IO_propValve_s9_2 | D28244 | WORD | -1
IO_waterLevel_0 | X1.0 | BOOL | FALSE | x | Water level
IO_waterLevel_1 | X1.1 | BOOL | FALSE | x | Water level
IO_waterLevel_2 | X1.2 | BOOL | FALSE | x | Water level
IO_waterLevel_3 | X1.3 | BOOL | FALSE | x | Water level
IO_waterLevel_4 | X1.4 | BOOL | FALSE | x | Water level
IO_waterLevel_5 | X1.5 | BOOL | FALSE | x | Water level
IO_clogSensor_0 | X1.6 | BOOL | FALSE
IO_clogSensor_1 | X1.7 | BOOL | FALSE
IO_solenoid_0 | Y1.0 | BOOL | FALSE
IO_solenoid_1 | Y1.1 | BOOL | FALSE
IO_solenoid_2 | Y1.2 | BOOL | FALSE
IO_solenoid_3 | Y1.3 | BOOL | FALSE
IO_pumpContact_0 | Y1.4 | BOOL | FALSE
IO_pumpContact_1 | Y1.5 | BOOL | FALSE
IO_pumpContact_2 | Y1.6 | BOOL | FALSE
IO_waterTemp_0 | D28302 | WORD | -1 | x
IO_waterTemp_1 | D28304 | WORD | -1 | x
IO_waterTemp_2 | D28306 | WORD | -1 | x
IO_waterTemp_3 | D28308 | WORD | -1 | x
IO_waterTemp_4 | D28310 | WORD | -1 | x
IO_waterTemp_5 | D28312 | WORD | -1 | x
IO_waterTemp_6 | D28314 | WORD | -1 | x
IO_waterTemp_7 | D28316 | WORD | -1 | x
IO_waterTemp_8 | D28322 | WORD | -1 | x
IO_waterTemp_9 | D28324 | WORD | -1 | x
IO_waterTemp_10 | D28326 | WORD | -1 | x
IO_waterTemp_11 | D28328 | WORD | -1 | x
IO_waterTemp_12 | D28330 | WORD | -1 | x
IO_waterTemp_13 | D28332 | WORD | -1 | x
IO_waterTemp_14 | D28334 | WORD | -1 | x
IO_waterTemp_15 | D28336 | WORD | -1 | x
IO_waterTemp_16 | D28342 | WORD | -1 | x
IO_waterTemp_17 | D28344 | WORD | -1 | x
IO_waterTemp_18 | D28346 | WORD | -1 | x
IO_waterTemp_19 | D28348 | WORD | -1 | x
IO_lightIntensity_0 | D28362 | WORD | -1
IO_lightIntensity_1 | D28364 | WORD | -1
IO_lightIntensity_2 | D28366 | WORD | -1
IO_lightIntensity_3 | D28368 | WORD | -1
IO_lightIntensity_4 | D28382 | WORD | -1
IO_lightIntensity_5 | D28384 | WORD | -1
IO_lightIntensity_6 | D28386 | WORD | -1
IO_lightIntensity_7 | D28388 | WORD | -1
IO_lightIntensity_8 | D28402 | WORD | -1
IO_lightIntensity_9 | D28404 | WORD | -1
IO_lightOnOff_0 | D28420.0 | BOOL | FALSE
IO_lightOnOff_1 | D28420.1 | BOOL | FALSE
IO_lightOnOff_2 | D28420.2 | BOOL | FALSE
IO_lightOnOff_3 | D28420.3 | BOOL | FALSE
IO_lightOnOff_4 | D28420.4 | BOOL | FALSE
IO_lightOnOff_5 | D28420.5 | BOOL | FALSE
IO_lightOnOff_6 | D28420.6 | BOOL | FALSE
IO_lightOnOff_7 | D28420.7 | BOOL | FALSE
IO_lightOnOff_8 | D28422.0 | BOOL | FALSE
IO_lightOnOff_9 | D28422.1 | BOOL | FALSE
MB_pump0_wStartStop | D25150 | WORD | -1 |  | Start stop
MB_pump0_wFreqCmd | D25151 | WORD | -1 |  | Frequency command
MB_pump0_wInputSrc | D25152 | WORD | -1 |  | Freq command source
MB_pump0_wPidFbkTerm | D25153 | WORD | -1 |  | Terminal session for PID feedback
MB_pump0_wPidTrgtSrc | D25154 | WORD | -1 |  | PID target source
MB_pump0_wPidTrgtVal | D25155 | WORD | -1 |  | PID target value
MB_pump0_rOutputHz | D25102 | WORD | -1 | x | Actual output freq
MB_pump0_rAciVal | D25112 | WORD | -1 |  | ACI val
MB_pump0_rVfdStatus | D25001 | WORD | -1 |  | VFD status
MB_pump0_rVfdMode | D25135 | WORD | -1
MB_pump0_faultRecord | D25160 | ARRAY [10] OF WORD | [10(-1)] | x | History of faults
MB_pump1_wStartStop | D25350 | WORD | -1 |  | Start stop
MB_pump1_wFreqCmd | D25351 | WORD | -1 |  | Frequency command
MB_pump1_wInputSrc | D25352 | WORD | -1 |  | Freq command source
MB_pump1_wPidFbkTerm | D25353 | WORD | -1 |  | Terminal session for PID feedback
MB_pump1_wPidTrgtSrc | D25354 | WORD | -1 |  | PID target source
MB_pump1_wPidTrgtVal | D25355 | WORD | -1 |  | PID target value
MB_pump1_rOutputHz | D25302 | WORD | -1 | x | Actual output freq
MB_pump1_rAciVal | D25312 | WORD | -1 |  | ACI val
MB_pump1_rVfdStatus | D25201 | WORD | -1 |  | VFD status
MB_pump1_rVfdMode | D25335 | WORD | -1
MB_pump1_faultRecord | D25360 | ARRAY [10] OF WORD | [10(-1)] | x | History of faults
MB_pump2_wStartStop | D25550 | WORD | -1 |  | Start stop
MB_pump2_wFreqCmd | D25551 | WORD | -1 |  | Frequency command
MB_pump2_wInputSrc | D25552 | WORD | -1 |  | Freq command source
MB_pump2_wPidFbkTerm | D25553 | WORD | -1 |  | Terminal session for PID feedback
MB_pump2_wPidTrgtSrc | D25554 | WORD | -1 |  | PID target source
MB_pump2_wPidTrgtVal | D25555 | WORD | -1 |  | PID target value
MB_pump2_rOutputHz | D25502 | WORD | -1 | x | Actual output freq
MB_pump2_rAciVal | D25512 | WORD | -1 |  | ACI val
MB_pump2_rVfdStatus | D25401 | WORD | -1 |  | VFD status
MB_pump2_rVfdMode | D25535 | WORD | -1
MB_pump2_faultRecord | D25560 | ARRAY [10] OF WORD | [10(-1)] | x | History of faults
MB_EmergencyStop | D25600.0 | BOOL | FALSE |  | Trigger for Emergency stop
Xfer_airflowVfdStartStop | D29000 | WORD | -1 |  | Airflow VFD in PLC2
Xfer_airflowVfdFreqCmd | D29001 | WORD | -1 |  | Airflow VFD in PLC2
Xfer_airflowVfdInputSrc | D29002 | WORD | -1 |  | Airflow VFD in PLC2
Xfer_airflowVfdStatusMonitor | D29003 | ARRAY [23] OF WORD | [23(-1)] | x | Status Airflow VFD in PLC2
tmpConversionFloat | D200 | REAL | 0
sensorWindSpeed | D26000 | ARRAY [30] OF WORD | [30(0)] | x | Anemometer reading
aqmSensorTemperature | D26100 | ARRAY [30] OF WORD | [30(0)] | x | Temperature reading
aqmSensorHumidity | D26200 | ARRAY [30] OF WORD | [30(0)] | x | Humdity reading
aqmSensorCO2 | D26300 | ARRAY [30] OF WORD | [30(0)] | x | CO2 reading
errAnemometer | D26400 | ARRAY [30] OF WORD | [30(0)] | x | Anemometer error (0 = no error)
errAQM | D26500 | ARRAY [30] OF WORD | [30(0)] | x | AQM sensor error (0 = no error)
errorAirVFD | D27000 | WORD | 0 |  | PLC2 VFD error
errorPLC2system | D27001 | WORD | 0 |  | PLC2 system error
errorPLC2io | D27002 | WORD | 0 |  | PLC2 IO error
errorPLC2com | D27003 | WORD | 0 |  | PLC2 COM error

## HMI Internal
base_addr | var_name | var_type | addr_offset | comment
1000 | PUMP_0_SELECTED | BIT | 1
| PUMP_1_SELECTED | BIT | 1
| PUMP_2_SELECTED | BIT | 1
| PUMP_CHECK | WORD | 1
| PUMP_LOCK_SEMI_PART | BIT | 1
| PUMP_LOCK_MANU_PART | BIT | 1
| DUMMY_BIT | BIT | 1
| DUMMY_WORD0 | WORD | 1
| DUMMY_WORD1 | WORD | 1
| DUMMY_WORD2 | WORD | 1
| STRING | WORD | 20
| DUMMY_BIT_TRUE | BIT | 1
| DUMMY_BIT_FALSE | BIT | 1
| SEC0_LOCK_SEMI_PART | BIT | 1
| SEC0_LOCK_MANU_PART | BIT | 1
| SEC1_LOCK_SEMI_PART | BIT | 1
| SEC1_LOCK_MANU_PART | BIT | 1
| SEC2_LOCK_SEMI_PART | BIT | 1
| SEC2_LOCK_MANU_PART | BIT | 1
| SEC0_LOCK_LIGHT | BIT | 1
| SEC1_LOCK_LIGHT | BIT | 1
| SEC2_LOCK_LIGHT | BIT | 1
| SHELF_AUTO_WATER_REG_SIZE | WORD | 8
| SHELF_AUTO_CURRENT_NO | WORD | 1
| SHELF_AUTO_PLC_OFFSET_ADDR | WORD | 1
| SHELF_AUTO_OFFSET_ADDR | WORD | 1
| S0_WATER_ON_HH | WORD | 1
| S0_WATER_ON_MM | WORD | 1
| S0_WATER_OFF_HH | WORD | 1
| S0_WATER_OFF_MM | WORD | 1
| S0_LIGHT_ON_HH | WORD | 1
| S0_LIGHT_ON_MM | WORD | 1
| S0_LIGHT_OFF_HH | WORD | 1
| S0_LIGHT_OFF_MM | WORD | 1
| S1_WATER_ON_HH | WORD | 1
| S1_WATER_ON_MM | WORD | 1
| S1_WATER_OFF_HH | WORD | 1
| S1_WATER_OFF_MM | WORD | 1
| S1_LIGHT_ON_HH | WORD | 1
| S1_LIGHT_ON_MM | WORD | 1
| S1_LIGHT_OFF_HH | WORD | 1
| S1_LIGHT_OFF_MM | WORD | 1
| S2_WATER_ON_HH | WORD | 1
| S2_WATER_ON_MM | WORD | 1
| S2_WATER_OFF_HH | WORD | 1
| S2_WATER_OFF_MM | WORD | 1
| S2_LIGHT_ON_HH | WORD | 1
| S2_LIGHT_ON_MM | WORD | 1
| S2_LIGHT_OFF_HH | WORD | 1
| S2_LIGHT_OFF_MM | WORD | 1
| S3_WATER_ON_HH | WORD | 1
| S3_WATER_ON_MM | WORD | 1
| S3_WATER_OFF_HH | WORD | 1
| S3_WATER_OFF_MM | WORD | 1
| S3_LIGHT_ON_HH | WORD | 1
| S3_LIGHT_ON_MM | WORD | 1
| S3_LIGHT_OFF_HH | WORD | 1
| S3_LIGHT_OFF_MM | WORD | 1
| S4_WATER_ON_HH | WORD | 1
| S4_WATER_ON_MM | WORD | 1
| S4_WATER_OFF_HH | WORD | 1
| S4_WATER_OFF_MM | WORD | 1
| S4_LIGHT_ON_HH | WORD | 1
| S4_LIGHT_ON_MM | WORD | 1
| S4_LIGHT_OFF_HH | WORD | 1
| S4_LIGHT_OFF_MM | WORD | 1
| S5_WATER_ON_HH | WORD | 1
| S5_WATER_ON_MM | WORD | 1
| S5_WATER_OFF_HH | WORD | 1
| S5_WATER_OFF_MM | WORD | 1
| S5_LIGHT_ON_HH | WORD | 1
| S5_LIGHT_ON_MM | WORD | 1
| S5_LIGHT_OFF_HH | WORD | 1
| S5_LIGHT_OFF_MM | WORD | 1
| S6_WATER_ON_HH | WORD | 1
| S6_WATER_ON_MM | WORD | 1
| S6_WATER_OFF_HH | WORD | 1
| S6_WATER_OFF_MM | WORD | 1
| S6_LIGHT_ON_HH | WORD | 1
| S6_LIGHT_ON_MM | WORD | 1
| S6_LIGHT_OFF_HH | WORD | 1
| S6_LIGHT_OFF_MM | WORD | 1
| S7_WATER_ON_HH | WORD | 1
| S7_WATER_ON_MM | WORD | 1
| S7_WATER_OFF_HH | WORD | 1
| S7_WATER_OFF_MM | WORD | 1
| S7_LIGHT_ON_HH | WORD | 1
| S7_LIGHT_ON_MM | WORD | 1
| S7_LIGHT_OFF_HH | WORD | 1
| S7_LIGHT_OFF_MM | WORD | 1
| S8_WATER_ON_HH | WORD | 1
| S8_WATER_ON_MM | WORD | 1
| S8_WATER_OFF_HH | WORD | 1
| S8_WATER_OFF_MM | WORD | 1
| S8_LIGHT_ON_HH | WORD | 1
| S8_LIGHT_ON_MM | WORD | 1
| S8_LIGHT_OFF_HH | WORD | 1
| S8_LIGHT_OFF_MM | WORD | 1
| S9_WATER_ON_HH | WORD | 1
| S9_WATER_ON_MM | WORD | 1
| S9_WATER_OFF_HH | WORD | 1
| S9_WATER_OFF_MM | WORD | 1
| S9_LIGHT_ON_HH | WORD | 1
| S9_LIGHT_ON_MM | WORD | 1
| S9_LIGHT_OFF_HH | WORD | 1
| S9_LIGHT_OFF_MM | WORD | 1
| S0_PLC_WORD_ADDR_OFFSET | WORD | 1
| S1_PLC_WORD_ADDR_OFFSET | WORD | 1
| S2_PLC_WORD_ADDR_OFFSET | WORD | 1
| S3_PLC_WORD_ADDR_OFFSET | WORD | 1
| S4_PLC_WORD_ADDR_OFFSET | WORD | 1
| S5_PLC_WORD_ADDR_OFFSET | WORD | 1
| S6_PLC_WORD_ADDR_OFFSET | WORD | 1
| S7_PLC_WORD_ADDR_OFFSET | WORD | 1
| S8_PLC_WORD_ADDR_OFFSET | WORD | 1
| S9_PLC_WORD_ADDR_OFFSET | WORD | 1
| S0_PLC_BIT_ADDR_OFFSET | WORD | 1
| S1_PLC_BIT_ADDR_OFFSET | WORD | 1
| S2_PLC_BIT_ADDR_OFFSET | WORD | 1
| S3_PLC_BIT_ADDR_OFFSET | WORD | 1
| S4_PLC_BIT_ADDR_OFFSET | WORD | 1
| S5_PLC_BIT_ADDR_OFFSET | WORD | 1
| S6_PLC_BIT_ADDR_OFFSET | WORD | 1
| S7_PLC_BIT_ADDR_OFFSET | WORD | 1
| S8_PLC_BIT_ADDR_OFFSET | WORD | 1
| S9_PLC_BIT_ADDR_OFFSET | WORD | 1
| VENTILATION_VFD_STATUS_FLAG | BIT | 1
| P0_START_TIME_HH | WORD | 1
| P0_START_TIME_MM | WORD | 1
| P0_END_TIME_HH | WORD | 1
| P0_END_TIME_MM | WORD | 1
| TMPWORD | WORD | 1
| USE_P0_SCHEDULE | BIT | 1

## PLC2 Global
variable_name | addr | type | init_value | comment
tmpConversionFloat | D200 | REAL | 0 | Used for real to word conversion
tmpCounter | D205 | INT | 0 | counter for delay
windSpeed | D1000 | ARRAY [30] OF WORD | [30(0)] | Anemometer reading in cm/s
airTemp | D1100 | ARRAY [30] OF WORD | [30(0)] | AQM reading
airHumidity | D1200 | ARRAY [30] OF WORD | [30(0)] | AQM reading
airCO2 | D1300 | ARRAY [30] OF WORD | [30(0)] | AQM reading
errAnemometer | D1400 | ARRAY [30] OF WORD | [30(0)] | Anemometer reading error
errAQM | D1500 | ARRAY [30] OF WORD | [30(0)] | AQM reading error
deviceReadState | D2000 | INT | 0
gDeviceIndex | D2001 | INT | 0
gDevice2Index | D2002 | INT | 0
CONST_NUM_ANEMOMETER | D2003 | INT | 0
CONST_NUM_AQM_SENSOR | D2004 | INT | 0
errorVFD | D3000 | WORD | 0 | Transfer VFD error flag to PLC1
errorSystem | D3001 | WORD | 0 | Transfer PLC system error to PLC1
errorIO | D3002 | WORD | 0 | Transfer PLC I/O error to PLC1
errorCOM | D3003 | WORD | 0 | Error in the COM port (ventilation sensors)