## Constants
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment | retain
20000 | shelf_no | 1 | WORD | 12 | x | total number of shelf
| snsr_no | 1 | WORD | 162
| snsr_data_reg_size | 1 | WORD | 6
| k_shelf_reg_size | 1 | WORD | 12 | x | how many register one shelf_data occupies
| k_shelf_modeIndexOffset | 1 | WORD | 0 |  | offset from shelf_x_addr to get shelf_x_mode
| k_shelf_autoWaterOnIndexOffset | 1 | WORD | 1 |  | offset from shelf_x_addr to get shelf_x_autoWaterOn
| k_shelf_autoLightOnIndexOffset | 1 | WORD | 2 |  | offset from shelf_x_addr to get shelf_x_autoLightOn
| k_shelf_autoLightIntensOffset | 1 | WORD | 3 |  | offset from shelf_x_addr to get shelf_x_autoLightIntens
| k_shelf_semiPVOnIndexOffset | 1 | WORD | 4 |  | offset from shelf_x_addr to get shelf_x_semiPVOn
| k_shelf_semiLightOnIndexOffset | 1 | WORD | 5 |  | offset from shelf_x_addr to get shelf_x_semiLightOn
| k_shelf_manuLightOnIndexOffset | 1 | WORD | 6 |  | offset from shelf_x_addr to get shelf_x_manuLightOn
| k_shelf_manuLightIntensIndexOffset | 1 | WORD | 7 |  | offset from shelf_x_addr to get shelf_x_manuLightIntens
| k_shelf_manuPvPosIndexOffset | 1 | WORD | 8 |  | offset from shelf_x_addr to get shelf_x_manuPVPos
| k_shelf_baseAddr | 1 | WORD | 10000 |  | baseAddr of all shelves
| secModeArr | 3 | ARRAY [3] OF WORD | [3(0)] | x | 1 - auto, 2- semiauto, 3 - manual
| sectionPvOnCountArr | 3 | ARRAY [3] OF WORD | [3(0)] |  | secPvCountArr[0]: number of PV to turn on in section 0
| k_sectionNo | 1 | WORD | 1 |  | total number of sections
| k_section0MaxShelfNo | 1 | WORD | 12 |  | maximum number of shelves for section 0
| k_section1MaxShelfNo | 1 | WORD | 12 |  | maximum number of shelves for section 1
| k_section2MaxShelfNo | 1 | WORD | 12 |  | maximum number of shelves for section 2
| flowratePerShelf_local | 1 | WORD | 14 |  | flowrate per shelf in lpm
| k_enablePumpRedundancy | 1 | BOOL | FALSE |  | whether to enable pump redundancy
| main_current_state | 12 | ARRAY [12] OF INT | [12(0)] |  | Main state machine current state (for each instance)
| main_next_state | 12 | ARRAY [12] OF INT | [12(0)] |  | Main state machine next state (for each instance)
| transition_current_state | 12 | ARRAY [12] OF INT | [12(0)] |  | PV transition state machine current state (for each instance)
| transition_next_state | 12 | ARRAY [12] OF INT | [12(0)] |  | PV transition state machine next state (for each instance)
| PVChangeMode | 1 | INT | 0
| delay_counter | 12 | ARRAY [12] OF WORD | [12(0)] |  | Counter for delays
| lastPVvalue | 12 | ARRAY [12] OF WORD | [12(0)] |  | Store last PV value for comparison whether to run PV change sequence or not
| k_pump_no | 1 | WORD | 2 |  | Number of pumps to use
| pump_rampup_current_state | 3 | ARRAY [3] OF INT | [3(0)] |  | Pump ramp up state machine state
| pump_rampup_next_state | 3 | ARRAY [3] OF INT | [3(0)] |  | Pump ramp up state machine next state
| pump_rampup_current_value | 3 | ARRAY [3] OF WORD | [3(0)] |  | Pump ramp up value
| lastPumpTargetValue | 3 | ARRAY [3] OF WORD | [3(0)] |  | Pump ramp up previous value
| bRunPumpRampup | 3 | ARRAY [3] OF BOOL | [3(FALSE)] |  | Flag for each pump
| stat_water_vfd_power1 | 1 | BOOL | TRUE | x | Status for VFD power
| stat_water_vfd_comm1 | 1 | BOOL | TRUE | x | Status for VFD Comm
| stat_water_vfd_motor1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_vfd_pid1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_vfd_overload1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_vfd_other1 | 1 | BOOL | TRUE | x | Other VFD error
| stat_water_shelf_valvefault1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_shelf_overflow1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_temp_range1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_tank_levellow1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_tank_levelhigh1 | 1 | BOOL | TRUE | x | Status for water system
| stat_water_tank_sensor_unison1 | 1 | BOOL | TRUE | x | Status for water system
| stat_light_burned1 | 1 | BOOL | TRUE | x | Status for lighting system
| stat_light_powertrip1 | 1 | BOOL | TRUE | x | Status for lighting system
| stat_alarm_clear | 1 | BOOL | TRUE | x | Global alarm indicator
| stat_plc1_system | 1 | BOOL | TRUE | x | PLC1 system
| stat_plc1_io | 1 | BOOL | TRUE | x | PLC1 IO
| stat_energy_consumption | 1 | WORD | 0 | x | Energy power meter reading
| tmpCounter | 1 | INT | 0
| CONST_WATER_RANGE_MAX | 1 | WORD | 0 | x | Checking water temperature range
| CONST_WATER_RANGE_MIN | 1 | WORD | 0 | x | Checking water temperature range
| tmpReal | 2 | REAL | 0
| overflow_last_time | 12 | ARRAY [12] OF WORD | [12(0)] |  | Overflow last reading of SR396 used to determine whether 1 second has elapsed
| overflow_counter | 12 | ARRAY [12] OF WORD | [12(0)] |  | Overflow timer
| waterTempOffset | 4 | ARRAY [4] OF WORD | [4(0)] | x | Offset to water temperature
| waterTempOffsetNegative | 4 | ARRAY [4] OF BOOL | [4(FALSE)] | x | True if negative offset
| waterTempFinal | 4 | ARRAY [4] OF WORD | [4(0)] | x | Water temp after offset is included
| overflowLocal | 12 | ARRAY [12] OF BOOL | [12(FALSE)] | x | Overflow sensor
| scheduler_pvon_hh | 12 | ARRAY [12] OF WORD | [12(0)] |  | PV on Hr
| scheduler_pvon_mm | 12 | ARRAY [12] OF WORD | [12(0)] |  | PV on min
| scheduler_pvoff_hh | 12 | ARRAY [12] OF WORD | [12(0)] |  | PV off Hr
| scheduler_pvoff_mm | 12 | ARRAY [12] OF WORD | [12(0)] |  | PV off min
| scheduler_lighton_hh | 12 | ARRAY [12] OF WORD | [12(0)] |  | Light on Hr
| scheduler_lighton_mm | 12 | ARRAY [12] OF WORD | [12(0)] |  | Light on min
| scheduler_lightoff_hh | 12 | ARRAY [12] OF WORD | [12(0)] |  | Light off Hr
| scheduler_lightoff_mm | 12 | ARRAY [12] OF WORD | [12(0)] |  | Light off min
| scheduler_in_use | 12 | ARRAY [12] OF BOOL | [12(FALSE)] |  | Use scheduler or not
| scheduler_pv_value | 12 | ARRAY [12] OF WORD | [12(0)] |  | PV value for the scheduler
| scheduler_light_intensity | 12 | ARRAY [12] OF WORD | [12(0)] |  | Light intensity for the scheduler
| pump_force_off | 3 | ARRAY [3] OF BOOL | [3(FALSE)] |  | Pump kill switch

## Shelf
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment | retain
10000 | mode | 1 | WORD | 2 | x | shelf_x mode auto-1, semi-2, manual-3 |  | If there's any changes made here, please update accordingly in CONSTANTS sheet
| autoWaterOn | 1 | BOOL | FALSE | x
| autoLightOn | 1 | BOOL | FALSE | x
| autoLightIntensity | 1 | WORD | 0 | x
| semiPVOn | 1 | BOOL | FALSE | x
| semiLightOn | 1 | BOOL | FALSE | x
| manuLightOn | 1 | BOOL | FALSE | x
| manuLightIntensity | 1 | WORD | 0 | x
| manuPVPos | 1 | WORD | 0 | x
| exePVPos | 1 | WORD | 0
| exeLightIntensity | 1 | WORD | 0
| exeLightOn | 1 | WORD | 0

## Sensor List
base_addr | shelf_sensor | general_sensor
12000 | wPres0 | wFlow0
| wPres1 | wFlow1
| wPres2 | aFlow0
| wTemp0 | aFlow1
| wTemp1 | aFlow2
aFlow3
aFlow4
aFlow5
aFlow6
aFlow7
aFlow8
aFlow9
aFlow10
aFlow11
aFlow12
aFlow13
aFlow14
aFlow15
aFlow16
aFlow17
aFlow18
aFlow19
aFlow20
aFlow21
aFlow22
aFlow23
aFlow24
aTemp0
aTemp1
aTemp2
aTemp3
aTemp4
aTemp5
aTemp6
aTemp7
aTemp8
aTemp9
aTemp10
aTemp11
aTemp12
aTemp13
aTemp14
aTemp15
aTemp16
aTemp17
aTemp18
aTemp19
aTemp20
aTemp21
aTemp22
aTemp23
aTemp24
aCO2_0
aCO2_1
aCO2_2
aCO2_3
aCO2_4
aCO2_5
aCO2_6
aCO2_7
aCO2_8
aCO2_9
aCO2_10
aCO2_11
aCO2_12
aCO2_13
aCO2_14
aCO2_15
aCO2_16
aCO2_17
aCO2_18
aCO2_19
aCO2_20
aCO2_21
aCO2_22
aCO2_23
aCO2_24
aRH_0
aRH_1
aRH_2
aRH_3
aRH_4
aRH_5
aRH_6
aRH_7
aRH_8
aRH_9
aRH_10
aRH_11
aRH_12
aRH_13
aRH_14
aRH_15
aRH_16
aRH_17
aRH_18
aRH_19
aRH_20
aRH_21
aRH_22
aRH_23
aRH_24

## Sensor Data
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment | retain
- | value | 1 | WORD | 0
| state | 1 | WORD | 0
| err_u | 1 | WORD | 0
| warn_u | 1 | WORD | 0
| warn_l | 1 | WORD | 0
| err_l | 1 | WORD | 0

## Pump
base_addr | variable_name | addr_offset | type | init_value | hmi_tag | comment | retain
11000 | pump_e_OnArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_e_ValveOnArr | 1 | ARRAY [4] OF BOOL | [4(FALSE)] | x
| pump_e_FlowOrRpm | 1 | WORD | 0 | x | 1 - Flow, 2 - RPM
| pump_e_SetpointArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_h_Mode | 3 | ARRAY [3] OF WORD | [3(0)] | x | Pump mode: 1 - auto, 2 - manual flowrate, 3 - RPM
| pump_h_PumpSelect | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_h_FlowSetArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_h_RpmSetArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_ctrlModeFbkArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_runningFbkArr | 1 | ARRAY [3] OF BOOL | [3(FALSE)] | x
| pump_flowrateFbkArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pump_rpmFbkArr | 3 | ARRAY [3] OF WORD | [3(0)] | x
| pumpFillDrainMode | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Operation mode (FALSE - steady water supply, TRUE - on off mode)
| pumpFillDrainModeOn | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Turn on or off fill-drain mode
| pumpFillValue | 3 | ARRAY [3] OF WORD | [3(0)] | x | Fill-Drain mode Fill values
| pumpDrainValue | 3 | ARRAY [3] OF WORD | [3(0)] | x | Fill-Drain mode Drain values
| pumpFillModeFlag | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Whether it's currently in Fill mode (0) or Drain mode (1)
| pumpFillDrainTimer_s | 3 | ARRAY [3] OF WORD | [3(0)] |  | Temporary counter in seconds to determine the duration of fill and drain
| pumpFillDrainSecondCounter | 3 | ARRAY [3] OF WORD | [3(0)] |  | Temporary counter to get a duration in seconds
| pumpFillDuration_s | 3 | ARRAY [3] OF WORD | [3(0)] | x | Fill duration in seconds
| pumpDrainDuration_s | 3 | ARRAY [3] OF WORD | [3(0)] | x | Drain duration in seconds
| pumpFillDrainCountDownTimer_s | 3 | ARRAY [3] OF WORD | [3(0)] | x | Countdown timer
| pumpAbnormalFlag | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Flag indicate something is abnormal
| pumpAbnormalityStartTime | 3 | ARRAY [3] OF WORD | [3(0)] |  | Anormality start time
| pumpAbnormalTermination | 3 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Pump stopped due to prolonged abnormality
| pumpTerminationThreshold_hz | 1 | WORD | 45 | x | Pump threshold in hz before termination
| pumpRecoverySequenceStarted | 3 | ARRAY [3] OF BOOL | [3(FALSE)] |  | flag to start recovery
| pumpRecoveryStartTime | 3 | ARRAY [3] OF WORD | [3(0)]
| flowratePerShelf | 3 | ARRAY [3] OF WORD | [3(32)] | x | flowrate per shelf in lpm

## IO Mapping
variable_name | addr | type | init_value | hmi_tag | comment | retain
IO_propValve_s0 | D28122 | WORD | -1
IO_propValve_s1 | D28124 | WORD | -1
IO_propValve_s2 | D28126 | WORD | -1
IO_propValve_s3 | D28128 | WORD | -1
IO_propValve_s4 | D28142 | WORD | -1
IO_propValve_s5 | D28144 | WORD | -1
IO_propValve_s6 | D28146 | WORD | -1
IO_propValve_s7 | D28148 | WORD | -1
IO_propValve_s8 | D28162 | WORD | -1
IO_propValve_s9 | D28164 | WORD | -1
IO_propValve_s10 | D28166 | WORD | -1
IO_propValve_s11 | D28168 | WORD | -1
IO_Valve_Fault_0 | X3.8 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_1 | X3.9 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_2 | X3.10 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_3 | X3.11 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_4 | X3.12 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_5 | X3.13 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_6 | X3.14 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_7 | X3.15 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_8 | X4.0 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_9 | X4.1 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_10 | X4.2 | BOOL | FALSE |  | Valve fault indicator
IO_Valve_Fault_11 | X4.3 | BOOL | FALSE |  | Valve fault indicator
IO_Overflow_0_0 | X1.12 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_0_1 | X1.13 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_1_0 | X1.14 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_1_1 | X1.15 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_2_0 | X2.0 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_2_1 | X2.1 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_3_0 | X2.2 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_3_1 | X2.3 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_4_0 | D3106.0 | BOOL | FALSE | x | TEMPORARY NEED TO CHANGE ***
IO_Overflow_4_1 | D3107.0 | BOOL | FALSE | x | TEMPORARY NEED TO CHANGE ***
IO_Overflow_5_0 | X2.4 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_5_1 | X2.5 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_6_0 | X2.6 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_6_1 | X2.7 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_7_0 | X2.8 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_7_1 | X2.9 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_8_0 | X2.10 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_8_1 | X2.11 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_9_0 | X2.12 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_9_1 | X2.13 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_10_0 | X2.14 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_10_1 | X2.15 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_11_0 | X3.0 | BOOL | FALSE | x | Overflow sensor
IO_Overflow_11_1 | X3.1 | BOOL | FALSE | x | Overflow sensor
IO_Tank_Overflow_Sensor_0 | X3.2 | BOOL | FALSE |  | Water tank sensor
IO_Tank_Overflow_Sensor_0 | X3.3 | BOOL | FALSE |  | Water tank sensor
IO_Tank_Full_Sensor_0 | X3.4 | BOOL | FALSE |  | Water tank sensor
IO_Tank_Full_Sensor_1 | X3.5 | BOOL | FALSE |  | Water tank sensor
IO_Tank_Empty_0 | X3.6 | BOOL | FALSE |  | Water tank sensor
IO_Tank_Empty_0 | X3.7 | BOOL | FALSE |  | Water tank sensor
IO_LED_Feedback_0 | X1.0 | BOOL | FALSE |  | TEMPORARY NEED TO CHANGE ***
IO_LED_Feedback_1 | X1.1 | BOOL | FALSE |  | TEMPORARY NEED TO CHANGE ***
IO_LED_Feedback_2 | X1.2 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_3 | X1.3 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_4 | X1.4 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_5 | X1.5 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_6 | X1.6 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_7 | X1.7 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_8 | X1.8 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_9 | X1.9 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_10 | X1.10 | BOOL | FALSE |  | Light control feedback
IO_LED_Feedback_11 | X1.11 | BOOL | FALSE |  | Light control feedback
IO_lightOnOff_0 | Y1.0 | BOOL | FALSE |  | Light control
IO_lightOnOff_1 | Y1.1 | BOOL | FALSE |  | Light control
IO_lightOnOff_2 | Y1.2 | BOOL | FALSE |  | Light control
IO_lightOnOff_3 | Y1.3 | BOOL | FALSE |  | Light control
IO_lightOnOff_4 | Y1.4 | BOOL | FALSE |  | Light control
IO_lightOnOff_5 | Y1.5 | BOOL | FALSE |  | Light control
IO_lightOnOff_6 | Y1.6 | BOOL | FALSE |  | Light control
IO_lightOnOff_7 | Y1.7 | BOOL | FALSE |  | Light control
IO_lightOnOff_8 | Y1.8 | BOOL | FALSE |  | Light control
IO_lightOnOff_9 | Y1.9 | BOOL | FALSE |  | Light control
IO_lightOnOff_10 | Y1.10 | BOOL | FALSE |  | Light control
IO_lightOnOff_11 | Y1.11 | BOOL | FALSE |  | Light control
IO_lightIntensity_0 | D28182 | WORD | -1 |  | No light
IO_lightIntensity_1 | D28184 | WORD | -1 |  | No light
IO_lightIntensity_2 | D28186 | WORD | -1 |  | Light intensity
IO_lightIntensity_3 | D28188 | WORD | -1 |  | Light intensity
IO_lightIntensity_4 | D28202 | WORD | -1 |  | Light intensity
IO_lightIntensity_5 | D28204 | WORD | -1 |  | Light intensity
IO_lightIntensity_6 | D28206 | WORD | -1 |  | Light intensity
IO_lightIntensity_7 | D28208 | WORD | -1 |  | Light intensity
IO_lightIntensity_8 | D28222 | WORD | -1 |  | Light intensity
IO_lightIntensity_9 | D28224 | WORD | -1 |  | Light intensity
IO_lightIntensity_10 | D28226 | WORD | -1 |  | Light intensity
IO_lightIntensity_11 | D28228 | WORD | -1 |  | Light intensity
IO_Temp_T0 | D28100 | WORD | -1 |  | Sump temp sensor
IO_Temp_T1 | D28102 | WORD | -1 |  | Container 0 return temp sensor
IO_Temp_T2 | D28104 | WORD | -1 |  | Container 1 return temp sensor
IO_Temp_T3 | D28106 | WORD | -1 |  | Container 2 return temp sensor
MB_pump0_wStartStop | D25150 | WORD | -1 |  | Start stop
MB_pump0_wFreqCmd | D25151 | WORD | -1 |  | Frequency command
MB_pump0_wInputSrc | D25152 | WORD | -1 |  | Freq command source
MB_pump0_wPidFbkTerm | D25153 | WORD | -1 |  | Terminal session for PID feedback
MB_pump0_wPidTrgtSrc | D25154 | WORD | -1 |  | PID target source
MB_pump0_wPidTrgtVal | D25155 | WORD | -1 |  | PID target value
MB_pump0_rOutputHz | D25102 | WORD | -1 | x | Actual output freq
MB_pump0_rAciVal | D25112 | WORD | -1 |  | ACI val
MB_pump0_rVfdStatus | D25001 | WORD | -1 |  | VFD status
MB_pump0_rVfdMode | D25135 | WORD | -1
MB_pump0_faultRecord | D25160 | ARRAY [10] OF WORD | [10(-1)] | x | History of faults
MB_pump1_wStartStop | D25350 | WORD | -1 |  | Start stop
MB_pump1_wFreqCmd | D25351 | WORD | -1 |  | Frequency command
MB_pump1_wInputSrc | D25352 | WORD | -1 |  | Freq command source
MB_pump1_wPidFbkTerm | D25353 | WORD | -1 |  | Terminal session for PID feedback
MB_pump1_wPidTrgtSrc | D25354 | WORD | -1 |  | PID target source
MB_pump1_wPidTrgtVal | D25355 | WORD | -1 |  | PID target value
MB_pump1_rOutputHz | D25302 | WORD | -1 | x | Actual output freq
MB_pump1_rAciVal | D25312 | WORD | -1 |  | ACI val
MB_pump1_rVfdStatus | D25201 | WORD | -1 |  | VFD status
MB_pump1_rVfdMode | D25335 | WORD | -1
MB_pump1_faultRecord | D25360 | ARRAY [10] OF WORD | [10(-1)] | x | History of faults
MB_EmergencyStop | D25600.0 | BOOL | FALSE |  | Trigger for Emergency stop
MB_power_Ia | D25715 | REAL | -1 |  | Power meter Ia total
MB_power_Ib | D25717 | REAL | -1 |  | Power meter Ib total
MB_power_Ic | D25719 | REAL | -1 |  | Power meter Ic total
MB_power_kw | D25729 | REAL | -1 |  | Power meter Kw total
tmpConversionFloat | D200 | REAL | 0
FEEDBACK_ESTOP_Status | D250.0 | BOOL | 0 |  | E-stop
REF_Rack_Type | D300 | WORD | 0 | x | Type A(1), B(2), undefined(0)
REF_version_major | D301 | WORD | 0 | x | Version info
REF_version_minor | D302 | WORD | 0 | x | Version info
REF_version_revision | D303 | WORD | 0 | x | Version info
REF_rack_id | D304 | WORD | 0 | x | Rack ID
REF_rtc | D310 | ARRAY [7] OF WORD | [7(0)] | x | Realtime clock
FEEDBACK_hmi_plugged_in | D320.0 | BOOL | 0 | x | HMI should set this to True
CTRL_apply_update | D321.0 | BOOL | 0 | x | Update all interface to actual addresses
FEEDBACK_shelf_stage_number | D3000 | ARRAY [12] OF WORD | [12(0)] | x | Control Shelf currently running stage
FEEDBACK_shelf_stage_percentage | D3020 | ARRAY [12] OF WORD | [12(0)] | x | Control Shelf stage duration percentage
FEEDBACK_shelf_numtray | D3040 | ARRAY [12] OF WORD | [12(0)] |  | Number of trays in shelf
CTRL_shelf_valve | D3060.0 | ARRAY [2] OF BOOL | [2(FALSE)] |  | Extra valve control for each rack
CTRL_pv_value | D4000 | ARRAY [12] OF WORD | [12(0)] |  | PV value set to actual hardware
FEEDBACK_led | D4020.0 | ARRAY [12] OF BOOL | [12(FALSE)] |  | LED feedback interface
FEEDBACK_led_intensity | D4022 | ARRAY [12] OF WORD | [12(0)] | x | Light intensity feedback
CTRL_pump_fill_drain_mode | D4050.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | CTRL for fill drain mode (false = normal, true = Fill drain mode)
CTRL_pump_fill_mode_flowrate | D4055 | ARRAY [3] OF WORD | [3(0)] | x | Control for fill mode (flowrate)
CTRL_pump_drain_mode_flowrate | D4060 | ARRAY [3] OF WORD | [3(0)] | x | Control for drain mode (flowrate)
CTRL_pump_fill_duration | D4065 | ARRAY [3] OF WORD | [3(0)] | x | Filling duration in sec
CTRL_pump_drain_duration | D4070 | ARRAY [3] OF WORD | [3(0)] | x | Draining duration in sec
FEEDBACK_fill_mode_flag | D4074.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Whether pump is currently running fill mode (true)
FEEDBACK_fill_drain_mode_on | D4075.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Scheduled fill drain mode (on when in FD mode, off when in normal mode)
FEEDBACK_fill_mode | D4076.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Filling (1) or draining (0)
FEEDBACK_fill_drain_remaining_time | D4077 | ARRAY [3] OF WORD | [3(0)] | x | Timer for fill drain mode before switching
CTRL_light_on | D4080.0 | ARRAY [12] OF BOOL | [12(FALSE)] |  | Assigned to turn light on/off (linked to hardware I/O)
CTRL_light_intensity | D4085 | ARRAY [12] OF WORD | [12(0)] |  | Light intensity set to hardware
CTRL_pump_mode | D4100 | ARRAY [3] OF WORD | [3(0)] | x | Pump operation mode (1 - auto, 2 - flowrate, 3 - RPM)
CTRL_pump_rpm_setpoint | D4105 | ARRAY [3] OF WORD | [3(0)] | x | RPM setpoint
CTRL_pump_flowrate_setpoint | D4110 | ARRAY [3] OF WORD | [3(0)] | x | Flowrate setpoint
FEEDBACK_pump_abnormal | D4115.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Check if pump is abnormal
FEEDBACK_pump_abnormal_termination | D4116.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Check if pump has terminated due to abnormal termination
REF_PVLookup_1_Arr | D4120 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 1 valves are on
REF_PVLookup_2_Arr | D4134 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 2 valves are on
REF_PVLookup_3_Arr | D4148 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 3 valves are on
REF_PVLookup_4_Arr | D4162 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 4 valves are on
REF_PVLookup_5_Arr | D4176 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 5 valves are on
REF_PVLookup_6_Arr | D4190 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 6 valves are on
REF_PVLookup_7_Arr | D4204 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 7 valves are on
REF_PVLookup_8_Arr | D4218 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 8 valves are on
REF_PVLookup_9_Arr | D4232 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 9 valves are on
REF_PVLookup_10_Arr | D4246 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 10 valves are on
REF_PVLookup_11_Arr | D4260 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 11 valves are on
REF_PVLookup_12_Arr | D4274 | ARRAY [12] OF WORD | [12(0)] |  | PV look-up values when only 12 valves are on
REF_ShelfSectionMapping_0_Arr | D4316 | ARRAY [12] OF WORD | [12(0)] | x | configure which shelves should belong to sec0
REF_ShelfSectionMapping_1_Arr | D4330 | ARRAY [12] OF WORD | [12(0)] | x | configure which shelves should belong to sec1
REF_ShelfSectionMapping_2_Arr | D4344 | ARRAY [12] OF WORD | [12(0)] | x | configure which shelves should belong to sec2
FEEDBACK_pump_rpm | D4358 | ARRAY [3] OF WORD | [3(0)] |  | RPM reading
FEEDBACK_pump_flowrate | D4361 | ARRAY [3] OF WORD | [3(0)] |  | Flowrate reading
REF_pump_flowrate_per_shelf_setpoint | D4364 | ARRAY [3] OF WORD | [3(0)] |  | Flowrate per shelf
CTRL_pump_pid_recovery | D4367.0 | ARRAY [3] OF BOOL | [3(FALSE)] |  | Recovery from PID ramp up of pump due to low water
FEEDBACK_pump_fill_drain_timer | D4370 | ARRAY [3] OF WORD | [3(0)] |  | Running timer for both fill and drain mode
CTRL_pump_on | D4400.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Pump on/off
FEEDBACK_overflow | D4405.0 | ARRAY [24] OF BOOL | [24(FALSE)] | x | Intermediate overflow indicator
CTRL_section_mode | D4460 | ARRAY [3] OF WORD | [3(0)] | x | Section mode: 1 - auto, 2 - semi, 3 - manual
CTRL_PV_on | D4465.0 | ARRAY [12] OF BOOL | [12(FALSE)] | x | Interface to PV on/off
CTRL_scheduler_pvon_hh | D4500 | ARRAY [12] OF WORD | [12(0)] | x | PV on Hr
CTRL_scheduler_pvon_mm | D4515 | ARRAY [12] OF WORD | [12(0)] | x | PV on min
CTRL_scheduler_pvoff_hh | D4530 | ARRAY [12] OF WORD | [12(0)] | x | PV off Hr
CTRL_scheduler_pvoff_mm | D4545 | ARRAY [12] OF WORD | [12(0)] | x | PV off min
CTRL_scheduler_lighton_hh | D4560 | ARRAY [12] OF WORD | [12(0)] | x | Light on Hr
CTRL_scheduler_lighton_mm | D4575 | ARRAY [12] OF WORD | [12(0)] | x | Light on min
CTRL_scheduler_lightoff_hh | D4590 | ARRAY [12] OF WORD | [12(0)] | x | Light off Hr
CTRL_scheduler_lightoff_mm | D4605 | ARRAY [12] OF WORD | [12(0)] | x | Light off min
CTRL_shelf_use_scheduler | D4620.0 | ARRAY [12] OF BOOL | [12(FALSE)] | x | Use scheduler or not
FEEDBACK_temp_sensor | D4630 | ARRAY [4] OF WORD | [4(0)] | x | Temp sensors
FEEDBACK_valve_setting | D4640 | ARRAY [12] OF WORD | [12(0)] | x | Valve value feedback
FEEDBACK_pump_on | D4655.0 | ARRAY [3] OF BOOL | [3(FALSE)] | x | Feedback whether pump is running
CTRL_scheduler_pv_value | D4660 | ARRAY [12] OF WORD | [12(0)] | x | Scheduler PV value
CTRL_scheduler_light_intensity | D4680 | ARRAY [12] OF WORD | [12(0)] | x | Scheduler Light intensity
REF_pump_spin_limit | D4700 | ARRAY [3] OF WORD | [3(0)] | x | Pump overspin limit
REF_pump_spin_limit_shutdown_time | D4705 | ARRAY [3] OF WORD | [3(10)] | x | Pump overspin limit time before shutdown
FEEDBACK_power_meter_KW | D4710 | REAL | 0 | x | Total Power reading in KW
FEEDBACK_power_meter_Ia | D4715 | REAL | 0 | x | Total Power reading in Ia
FEEDBACK_power_meter_Ib | D4720 | REAL | 0 | x | Total Power reading in Ib
FEEDBACK_power_meter_Ic | D4725 | REAL | 0 | x | Total Power reading in Ic
REF_pump_error_shutdown_recovery_time_m | D4730 | ARRAY [3] OF WORD | [3(10)]

## HMI Internal
base_addr | var_name | var_type | addr_offset | comment | retain
1000 | PUMP_0_SELECTED | BIT | 0

## PLC2 Global
variable_name | addr | type | init_value | comment | retain